SOAC Field vs CoolSheet Website — PVT Energy

Sydney Olympic Park  |  534.7 m² collector  |  aquatic (pool) preset  |  matched 19-day window

| Same 19-day window (2–20 Mar 2026) | Field measured | Website (default) | Website (SOAC collector) |
| --- | --- | --- | --- |
| PVT thermal (kWh) | 5,888 | 15,996 | 22,915 |
| PVT electricity (kWh) | not measured | 9,982 | 10,169 |
| Thermal: website ÷ field | 1.0× | 2.7× higher | 3.9× higher |

Why the website reads higher:

• Operating time — the real array generated for only ~111 hours over the 19 days (pump control, cloud, downtime); the model assumes the collector harvests whenever the sun is up.

• Real-world derating — the field delivers about 0.63× the ISO-predicted steady-state efficiency at matched bright-sun conditions (field η ≈ 0.20 vs predicted ≈ 0.32).

• Weather — the website uses a Typical Meteorological Year, not the actual (partly overcast) March 2026.

• Using SOAC's own lossy coefficients does not lower the estimate, because pool inlet water sits near ambient so the heat-loss term stays small.

Note: the field dataset has no PV-electricity sensor, so PVT electricity cannot be validated here — only the website estimate is shown. Website annual figures (PVT thermal ≈ 308,000 kWh default) are not comparable to a 19-day field window and are excluded.